## Sheet1
MHSP prediction equation constants for mean flow
Month | C | A1 | A2 | Catchment area (km sq) | Mean monsoon ppt (mm) | Gross head (m) | Transmission line length (km) | Transmission voltage (KV) | Mean monthly flow | Riparian Release | Design Discharge | Available Dischrage | Power output (MW) | No. of days | Energy o/p | Electrical power o/p (MW) | Plant factor (%)
January | 0.03117 | 0.8644 | 0 | 2423 | 618 | 182 | 22 | 132 | 26.2526 | 2.1142 | 26.4491 | 24.1384 | 34.7101 | 31 | 25.8243 | 38.0329 | 88.2988
February | 0.02417 | 0.8752 | 0 | [5 empty] | 22.1443 | 2.1142 | 26.4491 | 20.0302 | 28.8026 | 28 | 19.3554
March | 0.02053 | 0.8902 | 0 | [5 empty] | 21.1417 | 2.1142 | 26.4491 | 19.0275 | 27.3609 | 31 | 20.3565
April | 0.01783 | 0.9558 | 0 | [5 empty] | 30.6137 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 30 | 27.3837
May | 0.01193 | 0.9657 | 0 | [5 empty] | 22.1264 | 2.1142 | 26.4491 | 20.0122 | 28.7768 | 31 | 21.4099
June | 0.01135 | 0.9466 | 0.2402 | [5 empty] | 84.922 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 30 | 27.3837
July | 0.01641 | 0.9216 | 0.3534 | [5 empty] | 209.153 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 31 | 28.2964
August | 0.02592 | 0.9095 | 0.3242 | [5 empty] | 249.197 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 31 | 28.2964
September | 0.02206 | 0.8963 | 0.3217 | [5 empty] | 188.3053 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 30 | 27.3837
October | 0.01504 | 0.8772 | 0.2848 | [5 empty] | 87.2722 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 31 | 28.2964
November | 0.00792 | 0.8804 | 0.2707 | [5 empty] | 43.0359 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 30 | 27.3837
December | 0.00538 | 0.889 | 0.258 | [5 empty] | 28.8103 | 2.1142 | 26.4491 | 26.4491 | 38.0328 | 31 | 28.2964
[12 empty] | Total | 423.9131 | 365 | 309.6664
Constants for percentage flow equation
Dependent Variables | b | a | c | Q
Maximum flow(Qmax) | 0.812 | 0.5337 | 0.06141 | 1061.4222
25% exceedance | 0.9279 | 0.2986 | 0.012434 | 117.0382
45% exceedance | 0.9239 | 0.2018 | 0.0089146 | 43.6644
65% exceedance | 0.9044 | 0 | 0.024831 | 28.5633
85% exceedance | 0.9256 | 0 | 0.01449 | 19.6626
95% exceedance | 0.9531 | 0 | 0.0086449 | 14.5341
Minimum flow | 1.1689 | 0 | 0.0007382 | 6.6703